GENERIC SPECIFICATION

IPS Controller 9100

Mechanical and Electrical Details

The Integrated Pumping System (IPS) pump logic controller shall be Armstrong IPS Controller 9100. The IPS pump logic controller shall be specifically designed for the control of multiple pump HVAC heating and/or chilled water systems that involve up to 6 variable speed pumps operating in parallel or in standby configuration. The IPS pump logic controller shall allow field adjustments of control parameters as described below.

The IPS controller 9100 shall be capable of accepting and processing appropriate signals for the following dedicated terminal blocks:

- 18 analog inputs (AI) for zone differential pressure (DP) transmitter signals 4-20 mA

- 1 AI for DP transmitter pump run-out protection

- 6 digital inputs (DI) for pump DP switches (pump fault signals)

- 1 DI for remote connection for start/stop

- 6 DI’s for VFD fault signals

- 1 DI for alarm horn (buzzer)

- 1 DI for alarm silencer

- 6 analog outputs (AO) for VFD speed signals

- 6 digital outputs (DO) for pump run signals

- 4 DO’s for alarms:

  - pump/motor/VFD alarm,

  - DP transmitter alarm,

  - General system alarm and

  - Fatal alarm

- 6 DO’s for VFD automatic bypass run signals

- 6 AI’s for motor temperatures selectable between NTC or PT1000

- 6 DI’s for VFD run feedback signals

- 6 DI’s for VFD Bypass run feedback signals

- 4 AO’s for flow, kW, supply and return temperature sensors

- 1 serial port for communication with the BMS

- 1 serial port for communication with the VFD’s

The IPS pump logic controller shall have an internal circuit breaker and run on 230/1/50 power. The logic controller shall be based on Flash style memory, older style EEPROM style memory is unacceptable.

The IPS controller shall include a 10.4" back-lit touch-screen for all necessary user interface functions. Keypad based interfaces, LCD readouts and LED displays shall not be accepted. The IPS pump logic controller shall perform online self diagnostic testing of the CPU(s), RAM and flash memory. No data shall be lost during power supply interruptions.

The IPS pump logic controller shall have an IP54 rated cabinet. The IPS controller shall have three levels of password security: one level for field adjustable parameters, a second for factory / commissioning setup parameters and a third for BMS communication commissioning.

The IPS complies with the requirements for the following harmonised standards:

- Safety requirements for Low Voltage Switchgear & Controlgear Assemblies; BS EN 60439-1 (1999)

- Electromagnetic Compatibility (EMC) Part 6-3: Generic Standard;

Electromagnetic Compatibility (EMC) Emission Standard for Residential,

Commercial & Light-Industrial Environments.

BS EN 61326 Industrial, BS EN 55022, BS EN 55011, BS EN 61000-6-3 (2007)

- Electromagnetic Compatibility (EMC) Part 6-2 : Generic Standard;

Electromagnetic Compatibility (EMC) Immunity Standard for Industrial Environments.

BS EN 61326 Industrial, BS EN 61000-6-2 (2005)

The IPS conforms with the provisions of the following European Directives:

- Low Voltage Directive: 2006/95/EC

including all current amendments thereof.

- Electromagnetic Compatibility (EMC) Directive: 2004/108/EC

including all current amendments thereof.

Performance and Operating Logic

The IPS pump logic controller shall determine the most efficient combination of operating pumps and pump operating speed based on the zone DP sensor signals. The IPS pump logic controller shall respond to the most dissatisfied zone by increasing either, the number of operating pumps, or the pump speed. In the case where all zones are satisfied the IPS pump logic controller shall respond by decreasing either, the number of operating pumps, or the pump speed so as to optimize the energy efficiency of the pumping operation while meeting system demands. The IPS pump logic controller shall continuously monitor all zone signals to determine an active control zone. Use of a multiplexer for multiple sensor inputs is not acceptable. To prevent un-necessary changes to the operating pump speed, to become the active control zone, the candidate zone must have a greater error from setpoint than the current active control zone for greater than 5 minutes. This transition delay period, 5 minutes, shall be a password protected field adjustable parameter that can be altered by the user.

The IPS pump logic controller shall alternate the pumps based on a field adjustable interval of operating hours with a “bumpless” transfer algorithm. The logic controller shall incorporate embedded logic to prevent hunting, pump flow surge and motor overloading. The logic shall incorporate an adjustable PID control loop. PID control at the VFD is not acceptable.

Should one VFD/pump/by-pass unit fail, the appropriate alarm signal shall be activated. The standby VFD/pump unit shall be operated in variable speed mode. If the system demand is too great with the standby on VFD the IPS pump logic controller shall send (if enabled during commissioning) an automatic by-pass signal to each VFD/by-pass assembly to operate in by-pass.

Armstrong Integrated Limited S. A. Armstrong Limited

Wenlock Way23 Bertrand Avenue

Manchester Toronto, Ontario

United Kingdom, M12 5JL Canada, M1L 2P3

T: +44 (0) 8444 145 145T: 416-755-2291

F: +44 (0) 8444 145 146F: 416-759-9101© S.A. Armstrong Limited 2011

For Armstrong locations worldwide, please visit www. armstrongintegrated.comtc "For Armstrong locations worldwide, please visit www.armstrongpumps.com"

The IPS controller shall have Hand-Off-Automatic (H-O-A) control and shall provide the option for a remote on/off signal from a dry contact or BMS communication signal.

The IPS pump logic controller shall provide a data logging feature including alarms and events (adjustment to system parameters). The IPS pump logic controller shall offer the option for expanded memory of 4 megabytes for a rolling record of system parameters at 10 second intervals, with a time stamp.

The IPS pump logic controller shall be self prompting. All messages shall be displayed in plain English. The operator interface shall have: multi-fault memory and recall, on-screen help functions and separate user screens for:

- Zone setup including set-point and calibration of DP sensor range

- Pump setup including pump staging strategy (wire-to-water BEP, pump BEP and % pump speed)

- DP, flow, kW and temperature sensors setup

- BEP speed setup

- PID control parameters setup

- BMS communication setup

- Design set-point and end-of-curve data setup

- Alarm history and event review

- Display of zone, pump and system overview

- Display of system schematic showing operating pumps and operating parameters

- Factory default / commissioning setup data

The IPS Controller shall be capable of staging and de-staging operating pumps to yield the best wire-to-water efficiency of the hydronic system. This can be either done by receiving the VFD output kW consumption or by using a kW transmitter. Also the Controller shall be capable of displaying the wire-to-water efficiency continuously.

The IPS controller shall be capable of both hard-wired and serial communications with the BMS using Modbus, LonWorks, Trend and Metasys as standard protocols. The IPS controller shall offer the option of a gateway to communicate using BACnet or TCP/IP protocols.

The IPS pump logic controller shall automatically disable any zone differential pressure signals that are not within limits and alert the operator of a possible transmitter failure. Should all sensors fail or system failure be detected the pump speed will default to a pre-defined percent of full speed (factory default loaded as 90% of full speed). The IPS pump logic controller shall have a minimum speed limit entered as a field adjustable parameter (factory default loaded at 30% of full speed).