PFX Plate & Frame Heat Exchangers – 
AHRI 400 Specification

File No: 113.17

Date: December 19, 2023

Supersedes: 113.17

Date: October 14, 2015

Typical Specifications

- DESIGN

  - The unit shall be provided with a galvanized or stainless-steel OSHA splash shield.

  - The units shall be built in accordance with ASME code and when necessary be ASME code stamped board registered.

  - The unit shall be built in accordance with NSF 61 when the unit is required for domestic water applications.

- FRAME

  - The frame plate and pressure plate should be carbon steel SA 516 grade 70.

  - The frame and pressure plate shall be of sufficient thickness to meet the ASME design pressure. Stiffeners or support brackets are not allowed.

  - Carbon steel frame components shall be painted with Armstrong “Harvester Red” epoxy paint.

  - Units with 4" or greater connections shall be unlined or alloy-lined studded ports to mate with raised face or flat faced ANSI flanges. Rubber liners are not allowed.

  - Units with 2" or smaller connections shall have carbon steel female tapped NPT or male NPT connections if an alloy material is required.

  - Units with 2½" or 3" connections shall be with either studded ports or NPT as described above.

  - The frame design shall allow the thermal plates to be supported by the carry bar, top bar. The guide bar, bottom bar, shall only help properly align the plates.

  - A roller assembly from the carry bar shall support the pressure plate for units taller than 50".

  - Tightening bolts shall be zinc plated carbon steel SA193 B7.

- PLATES

  - Plates shall be constructed of Stainless Steel (304 or 316L) or Titanium.

  - Plates shall be pressed with a herringbone corrugation to optimize heat transfer.

  - Plates shall use an integral rolled edge hanging system to provide a rigid hanger device between the plate and carry bar and guide bar. Welded on hanging brackets or stiffeners are not acceptable.

  - Plates shall be permanently marked to indicate plate material and thickness.

  - Plates for all NSF 61 certified units designed for domestic water application are to be constructed of 316L Stainless Steel double wall pressed in a once-step stamping process.

- GASKETS

  - The gaskets shall be a one-piece construction with a double gasket barrier at the port region. The area isolated by the double gasket shall be vented to the atmosphere, so that a gasket failure is detected by leakage to the exterior prior to any possible cross contamination.

  - Gaskests are to be “mechanically fixed”. Glued gaskets are not acceptable.

  - The gaskets are to be made of NBR or EPDM depending on application.

  - Gaskets for all NSF 61 certified units designed for domestic water application are to be made of NBR or EPDM with an FDA approved material.

- SELECTION, CERTIFICATION AND TESTING

  - The manufacturer shall hydro-test the unit to 1.3 times the design pressure as directed by ASME Code.

  - The plate and frame heat exchangers must be selected in accordance with the AHRI 400 standard, and the unit must bear the AHRI certified sticker.

  - The plate and frame heat exchanger manufacturer must be a certified member of the AHRI 400 standard.

  - The manufacturer shall provide NSF 61 unit when the unit is required for domestic water applications.

  - The plate and frame heat exchanger manufacturer must be a certified member of NSF 61 - Drinking Water System Components - Health Effects.