TYPICAL SPECIFICATION

Armstrong Series 40MF End Suction Fire Pump Engine Driven - End Suction Fire Pump

1. PUMP

Supply and install as indicated on plans one (1) fire pump system consisting of one Armstrong Series 40MF, end suction fire pump listed by Underwriters Laboratories of Canada (ULC), Underwriters Laboratories Inc. (UL) and approved by Factory Mutual (FM). The pump shall be radically split, top center-line discharge, self venting casing. The pump construction shall be cast iron, bronze fitted and shall be fitted with packing. The shaft shall be fitted with stainless steel sleeves and be supported by two back to back thrust ball bearings and one radial roller bearing. The back pull out design shall allow the complete rotating assembly to be removed without disturbing the casing piping connections.

2. DIESEL ENGINE

The pump shall be direct coupled through flexible coupling to a diesel engine, specifically approved for fire pump services. Engine shall be supplied with all necessary accessories: cooling water system mounted on the engine,

storage batteries and fuel system.

3. SYSTEM

The fire pump shall be factory mounted and aligned with diesel engine on a common structural base. The fire pump package shall include all pump fittings such as gauges and relief valves and shall be supplied with an approved diesel engine controller.

4. TESTING

Fire pump shall be hydrostatically tested to a pressure recommended by UL, ULC or FM. It shall be subjected to a performance test at rated speed. A certified test curve shall be supplied with the pump. The SERIES 40MF, Model 4x3x13FM is the first in a series of end suction pumps that will be available from Armstrong for compact diesel applications.

4x3x13FM - Approved Range

| FLOW (USGPM) | HEAD (PSI) |
| --- | --- |
| 300 | 70-222 |
| 400 | 65-220 |
| 450 | 79-218 |
| 500 | 87-215 |
| 750 | 154-200 |

The pump is rated for fire at various diesel speeds such as 2350RPM, 2600RPM and 3000RPM. Contact your local representative for all the details.