TYPICAL SPECIFICATION

Series 4280 Starbloc Motor Mounted Pumps

- Provide as indicated on the plans and specifications, Armstrong single stage, end suction, motor mounted 4280 Starbloc centrifugal pumps, with rising head characteristics to pump shut off.

Refer to the schedule for pump flows and heads and motor speed, efficiency, enclosure and power requirements.

- The pumps shall be Armstrong 4280 Series motor mounted horizontal end suction pump.

Pump Construction:

- Pump casing shall be cast iron, suitable for 12bar working pressure at 65°C. (Ductile Iron for pressures to 17bar).

- The casing shall be hydrostatically tested to 150% maximum working pressure.

- The casing shall be radially split to allow removal of the rotating element without disturbing the pipe connections.

- The casing shall be equipped with a drilled and tapped drain connection. Suction and discharge connections shall be provided with drilled and tapped pressure gauge connections.

- For constant speed pumps over 1kW, impellers must be made of bronze, trimmed and then balanced to the design conditions specified. Balancing must be single-plane or two-plane as required by ISO 1940.  Maximum impeller trim to match the motor power is not acceptable

- Provide a stainless steel stub shaft, capable of easy serviceability.

- Mechanical Seal shall be single spring inside type with carbon face rotating against a silicone carbide

O-ring mounted seat, EPDM elastomer with stainless steel spring and hardware shall be provided.

- Motor power requirements shown on the pump schedule are the minimum acceptable and have been sized for continuous operation without exceeding the full load nameplate rating over the operating range of the pump curve, exclusive of service factor.