Design Envelope (including Permanent 
Magnet) 6800 Booster

File No: 100.6800

Date: August 03, 2021

Supersedes: New

Date: New

Typical Specifications

Part I: General

SCOPE

A. This specification covers the basic requirements for the design, materials, fabrication, inspection and testing, and handling of Design Envelope (Permanent Magnet) 6800 Boosters.

B. Domestic water Booster systems shall be verified by the manufacturer to provide the required duty point as specified on the submittals/drawings.

Quality Assurance

The manufacturer shall take single-source responsibility for complete package. The manufacturer shall have at least 15 years’ experience in the design, manufacturer, servicing, and support of variable speed booster packages.  The entire package shall be part of the manufacturer’s standard offering.  Custom packages shall not be accepted without validations of the manufacturer’s experience (as per above) with said packages.

Design Criteria

The drawings indicate the requirements as it relates to the components, capacity, and profiles of the booster package.  Booster packages having equal performance characteristics by other manufacturers may be considered, if deviations from weight, connection type and size and dimensions, do not change, as judged by the engineer. The burden of proof for equality is on the proposer.  The cost to accommodate deviations from the requirements is on the proposer.

Delivery and Storage

Store pumps in a dry location. Retain shipping flange protective covers and protective coatings during storage. Protect bearings and couplings against damage from sand, grit, and other foreign matter. Comply with manufacturers' rigging instructions for handling.

Part II: Products

Domestic Water Booster Package

All materials shall meet or exceed all applicable referenced standards, federal, state, and local requirements, and conform to codes and ordinances of authorities having jurisdiction.

Provide an Armstrong Design Envelope (Permanent Magnet) 6800 Booster Package model _______.  The design envelope shall encompass an initial design point of ______ USgpm (L/s) at _____ psi (kPa) head, which the package will be capable of supplying at ____% minimum efficiency level.  This design point shall be within the best efficiency region of the package between 100% and 80% nominal speed.

The dimensions of the package shall not exceed _____in W x _____in D x _____in H.  The weight of the booster package shall not exceed ______ lbs.  The booster package shall be delivered with both suction and discharge header shipped loose, to minimize damage and maximize ease during transport of the booster package into mechanical room.

Pumps

Each Vertical Multistage (VMS) pump will have the following pump characteristics:

- Rising heads to shut off to supply required hydrostatic lift in low flow conditions.

- Low axial thrust impeller to enable long motor bearing life.

- Air vent in casing cover allowing for proper venting to prevent air entrapment and dry run.

- Fill port in casing cover to allow for water fill, as well as installation of sensors, gauges, and other measuring devices.

- Self-Aligning liner ring, floating design constructed to prevent swelling at high temperatures.

- Keyed, direct drive pump and motor shafts for positive, reliable power transmission with no adjustments necessary

- “Flexible” floating outer casing allowing for thermal expansion in hot water applications, preventing deformation due to pressure fluctuations.

- Square-edge four spline shaft providing positive location and drive of impellers, eliminating wear.

- Cartridge mechanical seal design, enabling replacement of the shaft seal without disassembling the motor bracket.

- Spacer coupling allowing easy maintenance without having to remove heavy motors over 7 ½ HP.

Motors & Drives

Each pump shall be supplied with a ____hp, ____v/3/60,

- Permanent Magnet Motors: TEFC, Ultra High Efficiency IE5 (better than NEMA Super Premium) permanent magnet motor and a IP55 enclosure.  Ultra-High Efficiency IE5 permanent magnet motors shall be supplied with ECM drives with the following features: Power factor that varies between 0.5 and 0.8, with speed and load without the need for power factor correction circuits and C-UL Listed and CE Marked, EMI/EMC filters incorporated within the drive to ensure it meets the emission and immunity requirements of EN61800-3 to the 1st Environment Class C1 (EN55011 unrestricted sales class B).

- Induction Motors: _____ODP (TEFC), NEMA Premium® efficiency motor and an Armstrong UL Type-12 enclosure variable speed drive, which shall be integrated with the motor. Drives shall not be enclosed within the control panel.  NEMA Premium efficiency motors shall be supplied with variable speed drives with the following features: VVC-PWM type providing near unity displacement power factor (cos ø) without the need for external power factor correction capacitors at all loads and speeds, DC link chokes for the reduction of mains borne harmonic currents to reduce the DC link ripple current thereby increasing the DC link capacitors lifetime, UL and C-UL Listed and CE Marked showing compliance with both the EMC directive 89/336/EEC and the Low Voltage directive 72/23/EEC, RFI filters incorporated within the drive to ensure it meets the emission and immunity requirements of EN61800-3 to the 1st Environment Class C1 (EN55011 unrestricted sales class B), VFD and motor protection shall include: motor phase to phase fault, motor phase to earth fault, loss of supply phase, over voltage, under voltage, motor over temperature, inverter overload, over current.

Integrated controls and motor protection shall include:

- Motor phase to phase fault

- Motor phase to earth fault

- Loss of supply phase

- Over voltage, under voltage

- Motor over temperature

- Inverter overload, over current

Materials of construction

Pump

- Pump casing:

  - Vertical Multistage pumps (VMS 10, VMS 15, VMS 20) shall be of full 304 stainless steel construction.  Vertical Multistage pumps (VMS 32, VMS 45, VMS 64) shall have 304 stainless steel intermediate and outer casing with cast iron bottom casing and casing cover.  Pump connection shall be:

    - ANSI-250 flanges for working pressure to 370psig (25bar) at 250°F (120°C)

    - ANSI-150 flanges for working pressures to 232psig (16bar) at 250°F (120°C)

    - ANSI-300 flanges for working pressures to 400psig (27bar) at 250°F (120°C).

- Impeller: 304 stainless steel, fully enclosed type.

- Shaft: stainless steel pump shaft.

- Coupling: Rigid spacer type of brass or steel. Coupling to be designed to allow removal of all mechanical seal components for servicing without removal of the pump.

- Mechanical seals: Mechanical shaft seal with FPM® secondary seal, carbon rotating face and silicon carbide stationary seat.

- Bearing: Tungsten carbide lower pump bearings and sleeves providing maximum operating life.

Packaging

- Headers: 304 stainless steel.

- Base: Stainless steel.

- Panel support: Stainless steel.

Control panel

The control panel shall be of the programmable logic controller (PLC) type. The complete control panel assembly and all internal devices shall be UL508 and/or CSA labelled. The panel shall be complete with NEMA Type 4 Painted Steel Enclosure (STD) allowing for both indoor and outdoor use and as such will remain undamaged by ice formation on the enclosure. The panel shall include door interlocked main disconnect, watertight color graphic touchscreen display, windblown dust and falling dirt protection, fused drive connections, adjustable time delays, Hand-Off-Auto selector for each pump and minimum run timers. The control circuit shall include fault relay circuit to turn on the next pump should the lead pump fail.  The controller must be capable of controlling up to 5 pumps, with a 4-20 mA analogue signal using pressure as the control variable.

On-screen alarm display with alarm identification shall be incorporated with the following alarms included: low and high system pressure shutdown, low suction pressure or level shutdown, pump failure, drive fault, and suction and discharge pressure sensor failures. The controller shall include on-screen fault description and possible cause information with alarm horn for alarms.

The on-screen display will provide graphic representation of the booster package and include the following information: total flow, flow per pump, operating speed per pump, pump status.  Flow information shall be provided including Maximum flow in GPM​, Current flow in GPM​, Curves to illustrate consumption over time.  Energy information shall be provided including Monthly/yearly KWH consumption​, Instantaneous kw​, Capacity to reset​, Data charts for illustration on energy consumption versus time.

Non-volatile factory set parameters must be capable of being restored at any time in the field without requiring any programming device or connection to an external source. The controller must hold software in FLASH memory storage which prevents accidental loss of data due to voltage surge or spike.

All controls to be factory pre-wired and tested in accordance with provisions of the national electrical code. All control wires shall be individually numbered, and each component shall be labelled accordingly. All internal wiring shall be Copper stranded, A.W.G. with a minimum 90°F rating. The controller shall bear the UL508 label for industrial controls.

Pump sequencing

The pump designated as the lead pump shall start following a 5 second On-Delay time after sensing a drop in the system pressure 5 PSI below the desired set point value. The pump controller shall compare a signal from the discharge pressure transducer to the set point value and the lead pump speed shall ramp up in order to satisfy the set point pressure. The lag pump shall start following a 60 second On-Delay time, when the lead pump exceeds its best operating point (BOP), and a minimum run timer shall ensure that the lag pump runs for a minimum of 60 seconds. The lag pump shall ramp down in speed and turn off when the pumps that are running are operating at a point below the BOP and the lag pump minimum run timer has expired. The lead pump shall continue to operate and meet system requirements based on the set point value. The lead pump shall alternate every 24 hrs of operation where the second pump shall start and run for a period of 5 seconds, both pumps shall operate, the first pump on shall ramp down and the new lead pump shall continue to operate as above to meet system requirements.

Pump shutdown controls

All systems are equipped with a 'No-Flow' shutdown that will stop the pumps when the pump controller determines there has been a 'No-Flow' condition for a continuous 5-minute period. The lead pump will start again once a drop in pressure of at least 5 psi is measured on the discharge of the system.  To minimize maintenance cost, footprint, and single point of failure (for no flow shut) controls algorithms shall be capable of determining no flow conditions without requiring the presence of pressurized tanks.

Other Controls

Controller design shall include provisions for energy savings and maximum reliability:

- Conformance to ASHRAE 90.1, 201 Section 10.4.

- soft fill mode that automatically senses the need to fill plumbing systems and decreases ramp up and ramp down speeds to minimize hydraulic shock.

- pressure setback which eliminates the need for remote pressure transducer and associated cost by simulating remote sensing via local discharge sensor (per ASHRAE 90.1) and automatically reduces pressure setpoint as a function of flow.

- tank fill mode that enhances no flow shutdown by increasing pressure before system shutdown to fill hydro-pneumatic tanks, thus maximizing tank acceptance volume.

- emergency power mode to optimize emergency power scenarios by reducing total power draw from backup power sources.

- alternate setpoints to accommodate changes in design requirements i.e., overnight pressure washing, and cooling tower make up.

- best-operating-point (BOP) sequencing

- end of pump curve protection

- 24hr operation automatic alternation of pumps and built-in pump on-delay and minimum run timers, re-settable pump elapsed run time meters,

- on-screen field modifiable control and alarm parameters

- high suction pressure shutdown.

The system may be manually operated by means of the virtual Hand-off-Auto (HOA) selector buttons provided on the operator interface.

Instrumentation

Pump system shall be supplied with manifold mounted liquid filled pressure gauges for indicating suction and discharge pressure.

Factory prefabrication

The system shall be factory prefabricated, including butterfly isolation valves on the suction and discharge of each pump, silent check valves and lug style butterfly valves on the discharge allowing for maintenance of individuals pumps and valves without the need to disable entire booster, system piping shall connect to 2", 2.5", 3", 4", 6", 8" or 10" stainless steel headers with flanged connections which can be re-oriented from left to right side to maximize installation flexibility, steel base and panel support. All interconnecting piping shall be stainless steel. The only field connections required shall be piping to the system headers and one incoming power connection at the control panel.

Factory test

The booster system and its component parts shall undergo a complete operational flow test from zero to 100% design flow rate and design head under the specified suction pressure conditions. The system certification shall include copies of the test data as certified by a factory engineer. Performance test certifications should be placed inside the control panel and extra copies with an installation manual.

Certification

The entire system shall be third party certified by Underwriters Laboratories Inc. (UL) in accordance with OSHA 29 CFR with references to nationally recognized testing laboratories and by the National Sanitation Foundation (NSF) for NSF 61-2010, NSF-372-2010.  Full stainless-steel construction or NSF certification for individual components shall not be considered an adequate substitute for NSF-61 & NSF-372 certification for the system as a whole.

Warranty

The booster package shall be free from defects in material and workmanship under normal use and service for 18 months from installation but no more than 24 months from date of shipping, when registered with manufacturer and installed and used in accordance with manufacturer’s printed instructions (normal wear and tear excepted).

Manufacturers

The above specification describes equipment manufactured by Armstrong Fluid Technology., North Tonawanda, NY, USA. Alternate manufacturers of equipment will be considered provided that they are completely equal as to type, capacity and efficiency of pumps and controls. Alternate manufacturers' submittals must be certified by an officer of the company who is proposing that their system complies with the specifications in every detail.