FILE NO.: DATE: SUPERSEDES: DATE:

®

F43.210

JUNE 15. 1997

NEW

NEW

## TYPICAL SPECIFICATIONS

# VERTICAL IN-LINE FIRE PUMP – ELECTRIC MOTOR DRIVEN

1. PUMP

One Armstrong Darling Vertical In-line fire pump Model __________ listed by Underwriters Laboratories of Canada (ULC), Underwriters Laboratories Inc. (UL) and

approved by Factory Mutual (FM) having a capacity of _______________USGPM for a

pressure boost of _PSIG. (Suction pressure ________________PSIG, Discharge

pressure PSIG).

withstand rating of ________kAmps.

5. FIRE PUMP CONTROLLER AND AUTOMATIC TRANSFER SWITCH COMBINATION

The automatic transfer switch controller combination shall be approved by UL, ULC or FM, Model __________' The automatic transfer switch an the fire pump controller shall each be mounted in separate enclosure, mechanically attached to form one unit and provide for protected interlock wiring.

The pump shall have a bronze impeller, non corrosive shaft sleeve, packed gland with external flush line to the lantern ring suitable for 125 PSIG suction pressure. Pumps are supplied with cast iron casings incorporating a double volute design for sizes 4 x 3, 6 x 4 and 6 x 5.

The automatic transfer switch shall be capable of automatic power transfer from normal to an alternate __________ (generator I second utility) emergency power source in case of failure of normal supply and automatically re-transfer after restoration of normal power conditions.

2. ELECTRIC MOTOR

The pump shall be driven by a _______HP at _______RPM, _______Volts, _____Phase, ________Hz standard vertical close coupled open dripproof motor with a 1.15 service factor.

The automatic transfer switch shall incorporate an externally operated main isolating switch, a manual operating handle, indicators, contacts for remote alarms, voltage frequency and phase reversal sensing, time delays and memory circuit.

3. MINIMUM FITTINGS

The purnp shall be supplied with the following accessories: . One (1) 3½”dial type suction gauge

. One (1) 3½”dial type discharge gauge

. One (1) circulation relief valve

6. TESTING AND MOUNTING

The fire pump shall be hydrostatically tested to twice the maximum pressure developed at shut-off but not less than 250 PSI. Tests will meet or exceed NFPA 20 standards.

The fire pump shall be subjected to a performance test at rated speed.

4. FIRE PUMP CONTROLLER

The fire pump controller shall be listed and labeled by Underwriters Laboratories of Canada (ULC), by Underwriters Laboratories (UL) and 1 or approved by Factory

Mutual (FM). The fire pump controller shall be of the combined manual and automatic stop, _______________starting method, Model_______________,as manufactured

By_______________	. All equipment shall be enclosed in approved drip proof enclosures.

The control equipment shall be completely assembled, wired and tested at point of manufacture prior to shipment. Circuit breakers shall have an interrupting capacity or

The pump shall furnish not less than 150% of rated capacity at a pressure not less than 65% of rated head. The shut-off total head of the pump shall not exceed 140% of rated total head. Certified curves shall be supplied to the purchaser showing the efficiency, brake-horsepower and total head developed at shut-off at rated capacity and at 150% of rated capacity.

Following the tests, the fire pump shall be factory mounted and aligned with electric motor on a common structural base.

Armstrong Pumps Inc.	S.A. Armstrong Limited	Armstrong Pumps Limited	Armstrong Darling

93 East Avenue 	23 Bertrand Avenue	Peartree Road, Stanway	9001 De L'Innovation, Suite 200

North Tonawanda, New York 	Toronto, Ontario	Colchester, Essex	Montreal (Anjou), Quebec

U.S.A. 14120-6594	Canada, M1L 2P3	United Kingdom, CO3 0LP	Canada, H1J 2X9

Tel: (716) 693-8813	Tel: (416) 755-2291	Tel: +44 (0) 1206 579491	Tel: (514) 352-2424

Fax: (716) 693-8970	Fax: (416) 759-9101	Fax: +44 (0) 1206 760532	Fax: (514) 352-2425

www.armstrongpumps.com	© S.A. Armstrong Limited 2003