Fire Pump Accessories  |  Typical Specifications

File No: F51.153

Date: August 15, 2005

Supersedes: New

Date: New

For electric driver, constant speed sump pump:

The fire pump shall include the following accessories:

One (1) 3-1/2" discharge pressure gauge.

One (1) 1-1/2" air release valve with reducing flange.

One (1) discharge tee.

One (1) hose valve manifold, outside type.

One (1) set of _______ 2-1/2" hose valves with caps and chains.

One (1) FM approved flow meter.

For diesel driven, variable speed or when pump shut-off pressure exceeds the 
rated system pressure add:

One (1) main pressure relief valve.

One (1) ___ relief cone. (Open or closed type.)

One (1) relief tee.

For deep well pump add:

One (1) Water level indicator assembly: An airline of 1/4" (galvanized steel pipe), (copper tubing), (plastic tubing) shall be furnished of sufficient length to extend from the surface to the top of the bowl assembly. With it shall be furnished a direct reading (in feet) depth gauge of 4-1/2" diameter, hand pump and fittings.

For barrel pump add:

One (1) 3-1/2" suction gauge.