Electric Motor Fire Pump Controller  |

File No: F51.160

Date: August 15, 2005

Supersedes: New

Date: New

Typical Specifications

The fire pump controller shall be specifically approved for fire pump service by the (Underwriters Laboratories)

(Factory Mutual) Association, model                .

All equipment shall be enclosed in approved drip tight enclosure. The controller shall be of combined manual and automatic (limited service) (full voltage across-the-line) (primary resistance) (part winding) (autotransformer) (WYE Delta open or closed transition) type and incorporating the following:

- Disconnect switch - externally operable, quick break type (delete if limited service).

- Circuit breaker with trips in each phase, calibrated at least to 300% of the motor full load current. Capacity of the circuit breaker shall be amperes interrupting capacity.

- Motor starter capable of being energized automatically through the pressure switch or manually by an externally operable handle.

- The pressure switch set to cut in at              psig and out at               psig.

- Running period timer set to keep motor in operation when started automatically, for a minimum period of time, not exceeding seven minutes.

- Pilot lamp to indicate circuit breaker closed and power available.

- Ammeter test link and voltmeter test studs.

- Alarm relay to energize an audible or visible alarm through an independent source of power, to indicate circuit breaker open or power failure.

- Remote start switch relay.

The controller shall be fully assembled and factory tested by the controller manufacturer prior to shipment