TYPICAL SPECIFICATION

Flo-Trex Valves

Flo-Trex Valves

Furnish and install on the discharge side of each pump an Armstrong Model FTV Flo-Trex Combination Valve. Each

valve is to incorporate the following three functions in one body: Tight shut-off, spring-closure type silent non-slam

check and effective throttling with flow measurement capability. The body shall have (2) 1/4” NPT connections on

each side of the valve seat. Two connections to have brass pressure and temperature metering ports, with Nordel check valves and gasketed caps. Two other connections to be supplied with brass drain plugs. Metering ports are to be interchangeable with drain ports to allow for measurement flexibility when installed in tight locations. The valve disc shall be bronze plug & disc type with high impact engineered resin seat to ensure tight shut-off and silent check operation.

The valve stem shall be stainless steel with flat surfaces provided for adjustment with open-end wrench.

For Grooved Piping: Valve body shall be ductile iron with grooved ends and Armstrong anti-rotation ArmgripTM lugs

on the inlet and outlet of the body.

Flange adapters, where necessary, are to be Armstrong ArmgripTM PN16 or PN25 ductile iron flanges with antirotation lugs and EPT gaskets.

For Welded Flange Piping:

(For 10 bar flanges:) Valve body shall be Cast Iron with PN16 flanged ports.

(For 20 bar flanges:) Valve body shall be Ductile Iron with PN25 flanged ports.

The valve shall be selected and installed in accordance with the manufacturer’s instructions and be suitable for the

pressure and temperature specified.

Insulation (Available 2.5” – 6” Flo-Trex Valves)

Each valve shall be furnished with a pre-formed removable PVC insulation jacket to meet ASTM D1784 Class 14253-C, MEA #7-87, ASTM-E-84 and ASTM136 with a flame spread rating of 25 or less and a smoke development rating of 50 or less. There will be provided sufficient mineral fiberglass insulation to meet ASHRAE 90.1-1989 specifications in operating conditions with maximum Fluid Design Operating Temperature Range of 141°F-200°F (60°C-93°C) and Mean Rating Temperature of 125°F (52°C).