TYPICAL SPECIFICATION

Glycol Auto - Fill Units

Supply and install GLA glycol autofill unit complete with Armstrong expansion tank to control and provide expansion and maintain the glycol system pressure by providing glycol make-up automatically upon a drop in system pressure, for the following sealed system parameters:

- Total system liquid content _____________ gallons (liters)

- System flow temperature _____________ °F (°C)

- Static height above GLA unit _____________ feet (meters)

- Total boiler or chiller power _____________ HP or tons (kW)

- Maximum system operating pressure at GLA unit _____________ psi (kPa)

The Armstrong Expansion tank is to be suitable for the maximum pressure.

GLA Standard

The GLA Standard glycol autofill unit model GLA-S-LP-1 is to be provided with the following standard features:

- The GLA unit shall monitor and maintain the minimum system pressure at all times

- Low mixture cut-out level switches shall monitor the status of the mixing tank

- Level switches shall be 24 volt maximum to ensure intrinsic electrical safety

- Pump suction isolation valve

- Pump suction strainer

- Single phase power connection

- 45 psi (300 kPa) fill pressure