TYPICAL SPECIFICATION

Shallow Well Fire Pump - Water Lube for Static Water Level 50 feet or less

Supply and install as indicated on plans one (1) Armstrong fire pumping system (Listed by Underwriters Laboratories) (Factory Mutual Approved) consisting of:

One Armstrong model ______ vertical turbine fire pump (Listed by Underwriters Laboratories) (Factory Mutual Approved) having a capacity of _______ USgpm at _______ ft. total head for installation in a __________ inch diameter well.

Each pump shall deliver not less than 65% of rated head at 150% of capacity and shall have a shut-off head not to exceed 140% of rated head.

The total head includes pump discharge pressure at the discharge flange center line, pump column and discharge head losses, and lift below the center line of the discharge flange.

BOWL ASSEMBLY

The pump bowl assembly shall be Weir Floway pump type _________. The pump bowls shall be of close grain, cast iron ASTM A48 class 30 threaded or flanged.

A minimum of one-half inch diameter high tensile bolting shall be employed on flanged bowls. The water passages shall be lined with porcelain enamel to reduce friction losses, shall be free of blow holes, sand holes and other detrimental defects, and shall be accurately machined and fitted with bowl wear rings of bronze ASTM B505 alloy

943 or 954.

The impellers shall be of bronze ASTM B584 alloy 83800 enclosed and dynamically balanced. Impellers shall be securely fastened to the shaft with taper split bushings of steel. Impellers shall be adjusted vertically by an

external means.

The pump shaft shall be A582 grade 416 stainless steel, turned, ground and polished. It shall be supported by bronze bearings of ASTM B505 alloy C84400 above and below each impeller. The suction bearing shall be grease lubricated of the same material as the bowl bearing and be protected by a bronze sand collar of ASTM B584 alloy C83800. The size of the shaft shall be no less than that determined by ANSI/AWWA Specifications E101, Section A4.3,

paragraph 4.3.3.

The discharge case when used shall be threaded on the outside and fitted with a cast iron ASTM A48 Class 30 column adapter of the proper size to connect to the column selected.

The suction case shall be fitted with a corrosion resistant cone strainer with free area equal to four times the inlet area.

COLUMN ASSEMBLY

The unit shall be supplied with a column assembly to lengthen the pump so that the second impeller from the bottom is submerged at least 10 feet below the pumping water level at 150 percent to rated capacity. One foot additional submergence shall be added for each 1,000 feet of elevation above sea level.

The column size shall be such that friction loss will not exceed 5' per 100' based on the rated capacity of the pump. If possible, the column size shall also be such as to provide a velocity of not less than 5' per second at the rated capacity.

The outer column pipe shall be ASTM A53 grade B steel pipe or ASTM A120 in interchangeable sections not over 10' in length. All joints shall be connected with threaded sleeve type couplings or flanges. Flanges shall have a rabbet fit to insure accurate column alignment. Threaded sections shall be faced parallel and machined with 8 straight threads per inch permitting the ends to butt against the bearing retainer shoulder insure proper alignment and to secure the bearing retainer when assembled. The weight of the column pipe shall be no less than that stated in NFPA-20, Table 2 no. 4-3.2 "Pump Column Weights".

The line shafts shall be of carbon steel ASTM A108 grade C1045, turned and ground. They shall be furnished in interchangeable sections not over (10) feet in length. The butting faces shall be machined square to the axis of the shaft, with maximum permissible axial misalignment of the thread axis with the shaft axis 0.002" in 6". The size of the shaft shall be no less than that determined by ANSI/AWWA E101 Specifications, Section 5.5 for C1045 line shaft selection and shall be such that elongation due to hydraulic thrust will not exceed the axial clearance of the impellers in the pump bowls. Maximum run-out in 10' shall not exceed .005".

The line shafts shall be provided with ASTM A269 grade 304 stainless steel sleeves at the location of each line shaft bearing. The line shaft bearing shall be of 70 minimum shore hardness, neoprene, snap-in type, internally spiral grooved to flush out sand and other abrasives, mounted in ductile iron ASTM A536-77 bearing retainers held in position in the column coupling by means of the butted ends of the column pipe. Bearing spacing shall not exceed 10’. The line shafts shall be coupled with steel couplings ASTM A108, grade 1215 machined from solid bar stock and designed with safety factor of 1-1/2 times that of the line shaft. Each coupling shall have an inspection hole drilled in the center to assist in centering the line shafts in the coupling.

DISCHARGE HEAD ASSEMBLY

The discharge head shall be Weir Floway type “A” cast iron ASTM A48 Class 30 free of sand holes and other defects, or type “F” fabricated of carbon steel materials using ASTM A181 flanges, ASTM A53 Grade B body pipe and ASTM A36 steel plate and accurately machined with a rabbet fit on top to receive the driver. The discharge head shall be fitted with a 125/150# discharge flange where the shut-off head is 175 psi or less or a 250/300# flange where the shut-off pressure is between 175 and 400 psi. Flanges shall be arranged for through bolting and of the size shown on the plans.

The standard cast iron stuffing box shall be rated for 150# discharge pressure and shall be fitted with graphite acrylic packing and have either a lantern ring or grease chamber below the first packing ring. Throttle bearing shall be of high lead bronze ASTM B505 alloy C84400. The packing gland shall be of bronze ASTM B584 alloy C83800 with stainless steel bolting and with brass or stainless steel adjusting nuts. Sealing between the stuffing box and the discharge head shall be accomplished by means of and “O” ring.

If discharge pressure exceeds 150 psi, a high pressure by pass style packing box shall be supplied with a minimum of six rings of packing and two lantern rings, and a bypass line.

The top line shaft shall be ASTM A582 Grade 416 stainless steel and shall not exceed 10 feet in length. Impeller adjustment shall be provided at the top of the head shaft by means of a bronze adjusting nut of ASTM B584 alloy C83800 which shall be positively locked in position. The head shaft shall also be 416SS and shall be connected to the top line shaft beneath the driver to facilitate ease of assembly and maintenance.

The discharge head shall be fitted with an easily removable wire mesh shaft guard.

TESTING

Each fire pump shall be given a non-witnessed performance test and non-witnessed hydrostatic test of the discharge head and bowl assembly to NFPA-20 specifications at the factory before shipment. Minimum hydrostatic test pressure shall be twice shut-off pressure but not less than 250 psi.