TYPICAL SPECIFICATION

Suction Guides

Furnish and install on the suction of each pump an Armstrong Suction Guide, with Outlet Flow Stabilizing Guide Vanes, removable Stainless Steel Strainer and Fine Mesh Start-up Strainer.

For 150 psig flanged pipe system:  Supply Suction Guide with Cast Iron body with ANSI 125 flanged ports.

For 300 psig flanged pipe system:  Supply Suction Guide with Ductile Iron body and ANSI 250 flanged ports.

For grooved pipe system:  Supply Suction Guide with Ductile Iron body with Grooved inlet and ANSI 125 flanged outlet connections.

The mechanical contractor shall inspect the strainer prior to activating the pump and, further, shall remove the Fine Mesh Start-up Strainer after a short running period. (24 hours maximum). Space shall be provided for removal of the Strainer and connection of a Blow-down Valve.