TYPICAL SPECIFICATION

Vertical Turbine Fire Pumps

Supply and install as indicated on plans one (1) fire pump system consisting of:

1. PUMP

One model _____________ vertical turbine fire pump listed by Underwriters Laboratories Inc. (UL) and approved by Factory Mutual (FM) having a capacity of _________ USgpm for a pressure boost of _______ psig.

2. DIESEL ENGINE

The pump shall be direct connected through flexible coupling to a diesel engine, manufactured by __________, model _____________ UL and FM listed and approved with a net continuous rating of ______ hp at ______ rpm at ________ ft. of elevation above sea level. The diesel engine shall conform to the requirements of the National Fire Protection Association, Pamphlet #20 and shall be specifically approved for fire pump service. It shall operate at a rated speed not exceeding the above RPM and shall develop sufficient horsepower to drive the pump with 10% reserve power.

Cooling Water System

The cooling water supply for the heat exchanger shall be from the discharge of the pump, taken off prior to the pump discharge valve. The pipe connection shall include four (4) manual shut-off valves (including by-pass line), two strainers, two pressure regulators, a listed automatic solenoid valve and a pressure gauge, piping and fittings all fitted to engine, per NFPA 20, by the pump manufacturer.

Storage Batteries

Two heavy duty lead acid batteries shall be provided and furnished in a dry charge condition with electrolyte liquid in separate containers. Suitable battery rack and 60” of battery cables shall be included.

Right Angle Gear Drive

FM approved right angle gear drive shall be supplied with drive shaft rated for the maximum bhp of the pump. A suitable coupling guard shall be supplied to enclose rotating assemblies.

Fuel System

The fuel system shall be UL listed and shall consist of an above ground storage tank of _________ gallons as recommended per NFPA 20, fill pipe and cap, manual shut-off cock, flame arrestor, oil level gauge and braided flexible connectors. The tank shall be supplied with legs for floor mounting. Approved steel tubing and miscellaneous pipe and fittings shall be supplied by the mechanical contractor.

3. ELECTRIC MOTOR

The fire pump shall be coupled to a vertical hollow-shaft electric motor with a maximum hp of ___________ at ______ rpm, _________ Volt, _______ phase, _________ cycle. Motor shall be open drip proof, standard efficiency with 1.15 service factors.

4. MINIMUM FITTINGS

The pump shall be supplied with the following accessories:

- One (1) discharge gauge, 3½” (89 mm) dial type

- One (1) 1½” (38 mm) air release valve

5. OTHER ACCESSORIES

Pump shall be supplied with one (1) outside test header 2½” (63.5 mm) hose valves with caps and chains to suit the rated pump flow. One (1) main relief valve and one(1) waste cone shall be supplied.

6. AUTOMATIC DIESEL ENGINE CONTROLLER

The Fire Pump Controller shall be manufactured by ____________ model ____________ built strictly in accordance with the latest requirements of the NFPA. Controller shall be listed and labeled by Underwriters Laboratories of Canada (ULC) and/or Underwriters Laboratories (UL) and/or approved by Factory Mutual (FM).

7. JOCKEY PUMP

The jockey pump shall be model ______________ for a capacity of ___________ USgpm and a pressure boost of ____________ psig. The jockey pump shall be driven by an open drip proof electric motor of ______ hp,

______ rpm, ________ Volt, ______ phase, ______ cycle.

8. JOCKEY PUMP CONTROLLER

The jockey pump shall be controlled by an automatic jockey pump controller model ___________ with full voltage starter.

9. MOUNTING AND TESTING

The pump shall be suitable for a maximum working pressure of __________. Pump shall be hydrostatically tested at twice the maximum working pressure for at least 5 minutes.

The pump shall be performance tested at rated speed. The pump shall furnish not less than 150% of rated capacity at a pressure not less than 65% of rated head. The shut-off total head of the pump should not exceed 140% of total rated head. A certified test curve, indicating the flow, head, power and efficiency shall be supplied.